## Index
Index of spreadsheets
Tracer studies
Water Quality at challenge test
Microbial Challenge Low Flow
Microbial Challenge MS2+E.coli
Microbial Challenge HF(1)
Microbial Challenge HF(2)
Microbial Challenge HF(3)
Microbial Challenge HF(4)
Calc. Ventura Val.
Calc. Low before+high after

## Tracer studies
[6 empty] | Ventura data: | Seconds
Tracer Studies | [5 empty] | 1060 L/min Retention time between sampling ports 4 and 5 (seconds) = | 18
[6 empty] | 355 L/min Retention time between sampling ports 4 and 5 (seconds) = | 53.8986
Date | Temperature | Flow (L/min) | Ports | Time after start of rhodamine addition (seconds) | Fluorescence Reading | 1060 L/min Retention time between sampling ports 1 and 6 (seconds) = | 195
2015-04-21 | ambient | 285 GPM | 1 and 6 | 0
10
20
30
40
50
60
70
80
90
100
110
|  |  |  | 120 | 73.1
|  |  |  | 130 | 69.19
|  |  |  | 140 | 71.09
|  |  |  | 150 | 88.25
|  |  |  | 160 | 73.08
|  |  |  | 170 | 69.67
|  |  |  | 180 | 71.35
|  |  |  | 190 | 70.62
|  |  |  | 200 | 67.71
|  |  |  | 210 | 65.99
|  |  |  | 220 | 64.8
|  |  |  | 230 | 62.87
|  |  |  | 240 | 66.38
|  |  |  | 250 | 82.1
|  |  |  | 260 | 158.4
|  |  |  | 270 | 324.3
|  |  |  | 280 | 451.2
|  |  |  | 290 | 528.9
|  |  |  | 300 | 528.7
|  |  |  | 310 | 547.2
|  |  |  | 320 | 551.1
|  |  |  | 330 | 542.8
|  |  |  | 340 | 552.3
|  |  |  | 350 | 549
|  |  |  | 360 | 542.7
|  |  |  | 370 | 531
|  |  |  | 380 | 450.9
|  |  |  | 390 | 295.3
|  |  |  | 400 | 145.8
|  |  |  | 410 | 98.17
|  |  |  | 420 | 81
|  |  |  | 430 | 71.26
|  |  |  | 440 | 70.82
|  |  |  | 450 | 66.69
|  |  |  | 460 | 66.82
|  |  |  | 470 | 68.14
|  |  |  | 480 | 64.55
|  |  |  | 490 | 69.52
|  |  |  | 500 | 67.16
|  |  |  | 510 | 75.07
2015-04-21 | ambient | 284 GPM | 4 and 5 | 0 | 84.72
|  |  |  | 10 | 87.38
|  |  |  | 20 | 83.86
|  |  |  | 30 | 187.7
|  |  |  | 40 | 547.4
|  |  |  | 50 | 597.9
|  |  |  | 60 | 610.8
|  |  |  | 70 | 605.2
|  |  |  | 80 | 606.9
|  |  |  | 90 | 421.8
|  |  |  | 100 | 109.4
|  |  |  | 110 | 93.07
|  |  |  | 120 | 92.46
|  |  |  | 130 | 126.8
|  |  |  | 140 | 90.34
|  |  |  | 150 | 91.31
|  |  |  | 160 | 92.13
|  |  |  | 170 | 89.41
|  |  |  | 180 | 86.09
|  |  |  | 190 | 87.11
|  |  |  | 200 | 86.64
|  |  |  | 210 | 82.21
|  |  |  | 220 | 83.3
|  |  |  | 230 | 84.18
|  |  |  | 240 | 81.09
2015-04-21 | ambient | 140 GPM | 4 and 5 | 0 | 69.71
|  |  |  | 10 | 70.58
|  |  |  | 20 | 71.19
|  |  |  | 30 | 72.15
|  |  |  | 40 | 72.09
|  |  |  | 50 | 146
|  |  |  | 60 | 635.9
|  |  |  | 70 | 1017
|  |  |  | 80 | 1117
|  |  |  | 90 | 1140
|  |  |  | 100 | 1145
|  |  |  | 110 | 937.7
|  |  |  | 120 | 536.8
|  |  |  | 130 | 201.7
|  |  |  | 140 | 110.2
|  |  |  | 150 | 86.05
|  |  |  | 160 | 74.21
|  |  |  | 170 | 69.49
|  |  |  | 180 | 68.83
|  |  |  | 190 | 71.78
|  |  |  | 200 | 69.34
|  |  |  | 210 | 69.05
|  |  |  | 220 | 67.84
|  |  |  | 230 | 65.25
|  |  |  | 240 | 64.87

## Water Quality at challenge test
Water Quality on Challenge Test Days
[5 empty] | On-line |  |  | On-line | [6 empty] | On-line
Challenge test date | Challenge Test descriptor | Flow tested | Temperratures tested | Alkalinity | pH |  | Ca | Turbidity | SS | VSS |  | COD | TOC | EC | UVT
[7 empty] | (mg/L) |  |  | (mg/L) |  |  | (mg/L) | (uS/cm)
2015-04-22 | Low Flow | 1065 | 75, 72,69, 66 | 36 | 6.8 |  | 17 | 3.5 | 13 | 12 |  | 60 | 13 | 830 | 50
2015-04-24 | High Flow | 355 | 75, 72,69, 66 | 60 | 6.6 |  | 16 | 3.5 | 16 | 6 |  | 65 | 14 | 850 | 44
2015-04-27 | MS2+E,coli | 1065 | 66, 63, 60, 57 | 42 | 6.6 |  | 16 | 6.8 | 24 | 6 |  | 60 | 15 | 830 | 41
2015-05-27 | High Flow, Repeat 1 | 1065 | 75, 72, 69 | 59 | 6.9 |  | 18 | 4.6 | 24 | 4 |  | 70 | 15 | 890 | 35
2015-06-02 | High Flow, Repeat 2 | 1065 | 75, 72, 69 | 43 | 6.6 |  | 16 | 2.3 | 16 | 2 |  | 50 | 13 | 730 | 43
2015-06-23 | High Flow, Repeat 3 | 1065 | 75, 72, 69 | 53 | 6.7 |  | 17 | 9 | 23 | 33 |  | 44 | 16 | 830 | 40
Challenge Test Results
Test Date
| 2015-04-24 |  |  | 2015-05-27 |  |  |  |  | 2015-06-02 |  |  |  |  | 2015-06-23
Temp. | MS2 count (pfu/mL) | LV | LRV |  | Average | MS2 count (pfu/mL) | LV | LRV |  | Average | MS2 count (pfu/mL) | log (count) | LRV |  | Average | MS2 count (pfu/mL) | log (count) | LRV | Average
(°C)
75 | 0.3 | -0.52 | 4.5 |  | 4.2167 | 1.7 | 0.23 | 5.2 |  | 5.25 | 5 | 0.7 | 4.7 |  | 5 | 1.2 | 0.08 | 5.4 | 5.4667
| 1 | 0 | 4 |  |  | 1.3 | 0.11 | 5.3 |  |  | 1.8 | 0.26 | 5.2 |  |  | 3 | 0.48 | 5
| 1 | 0 | 4 |  |  | 2 | 0.3 | 5.1 |  |  | 7 | 0.85 | 4.6 |  |  | 1 | 0 | 5.4
| 0.2 | -0.7 | 4.7 |  |  | 1 | 0 | 5.4 |  |  | 2 | 0.3 | 5.1 |  |  | 0.7 | -0.15 | 5.6
| 2 | 0.3 | 3.7 |  |  | 1 | 0 | 5.4 |  |  | 1.5 | 0.18 | 5.3 |  |  | 0.3 | -0.52 | 6
| 0.4 | -0.35 | 4.4 |  |  | 2 | 0.3 | 5.1 |  |  | 2 | 0.3 | 5.1 |  |  | 1 | 0 | 5.4
72 | 79 | 1.9 | 2.1 |  | 2.1833 | 1370 | 3.14 | 2.3 |  | 2.4833 | 1110 | 3.05 | 2.4 |  | 2.3333 | 920 | 2.96 | 2.5 | 2.4333
| 80 | 1.9 | 2.1 |  |  | 820 | 2.91 | 2.5 |  |  | 1210 | 3.08 | 2.4 |  |  | 1150 | 3.06 | 2.4
| 65 | 1.81 | 2.2 |  |  | 1240 | 3.09 | 2.3 |  |  | 1190 | 3.08 | 2.4 |  |  | 950 | 2.98 | 2.5
| 50 | 1.7 | 2.3 |  |  | 960 | 2.98 | 2.5 |  |  | 1380 | 3.14 | 2.3 |  |  | 1030 | 3.01 | 2.4
| 79 | 1.9 | 2.1 |  |  | 480 | 2.68 | 2.8 |  |  | 1300 | 3.11 | 2.3 |  |  | 1020 | 3.01 | 2.4
| 47 | 1.67 | 2.3 |  |  | 950 | 2.98 | 2.5 |  |  | 1530 | 3.18 | 2.2 |  |  | 1170 | 3.07 | 2.4
69 | 2030 | 3.31 | 0.7 |  | 0.71667 | 38000 | 4.58 | 0.9 |  | 0.85 | 23500 | 4.37 | 1.1 |  | 1.0333 | 29700 | 4.47 | 1 | 0.98333
| 1610 | 3.21 | 0.8 |  |  | 51000 | 4.71 | 0.7 |  |  | 26700 | 4.43 | 1 |  |  | 27600 | 4.44 | 1
| 1930 | 3.29 | 0.7 |  |  | 53000 | 4.72 | 0.7 |  |  | 23500 | 4.37 | 1.1 |  |  | 26500 | 4.42 | 1
| 1920 | 3.28 | 0.7 |  |  | 38000 | 4.58 | 0.9 |  |  | 27200 | 4.43 | 1 |  |  | 26100 | 4.42 | 1
| 1980 | 3.3 | 0.7 |  |  | 43000 | 4.63 | 0.8 |  |  | 24500 | 4.39 | 1 |  |  | 28900 | 4.46 | 1
| 1950 | 3.29 | 0.7 |  |  | 21000 | 4.32 | 1.1 |  |  | 26800 | 4.43 | 1 |  |  | 31300 | 4.5 | 0.9

## Microbial Challenge Low Flow
Low flow MS2 challenge tests | [14 empty] | Test Conditions
[15 empty] | Time (sec) | Temperaure (F) (=75C) | Temperature (C) | Flow (GPM) | Flow (L/min) | Time (sec) | Temperaure (F) (=72C) | Temperature (C) | Flow (GPM) | Flow (L/min) | Time (sec) | Temperaure (F) (=69C) | Temperature (C) | Flow (GPM) | Flow (L/min) | Time (sec) | Temperaure (F) (=66C) | Temperature (C) | Flow (GPM) | Flow (L/min) | Time (sec) | Temperaure (F) (ambient) | Temperature (C) | Flow (GPM) | Flow (L/min)
Sample Date | Sample No. | Challenge Test No | Temperature (Deg.C) | Flow Rate (L/min) | Sample Port | Sample time (second) |  | MS2 Count (pfu/mL) | log (count) | Average (Log (count)) | SD (log(count)) | LRV | SD (LRV) | LRV | 0 | 167.2 | 75.1712 | 151 | 571.535 | 0 | 161.4 | 71.9464 | 153 | 579.105 | 0 | 156 | 68.944 | 149 | 563.965 | 0 | 150.9 | 66.1084 | 151 | 571.535 | 0 | 77.5 | 25.298 | 159 | 601.815
2015-04-22 | 6-75-355-5-1 | 6 | 75 | 355 | 5 | 0 |  | 0 |  | -0.30989 | 0.30121 | 5.2734 | 0.4313 | 5.7163 | 30 | 167 | 75.06 | 151 | 571.535 | 30 | 161.7 | 72.1132 | 153 | 579.105 | 30 | 156 | 68.944 | 152 | 575.32 | 30 | 150.9 | 66.1084 | 152 | 575.32 | 30 | 77.4 | 25.2424 | 149 | 563.965
| 6-75-355-5-2 |  |  |  |  | 10 |  | 0 | [6 empty] | 60 | 167 | 75.06 | 150 | 567.75 | 60 | 161.8 | 72.1688 | 150 | 567.75 | 60 | 156.1 | 68.9996 | 151 | 571.535 | 60 | 150.9 | 66.1084 | 151 | 571.535 | 60 | 77.4 | 25.2424 | 150 | 567.75
| 6-75-355-5-3 |  |  |  |  | 20 |  | 0 | [6 empty] | 90 | 167.1 | 75.1156 | 151 | 571.535 | 90 | 161.9 | 72.2244 | 150 | 567.75 | 90 | 156 | 68.944 | 149 | 563.965 | 90 | 151 | 66.164 | 149 | 563.965 | 90 | 77.4 | 25.2424 | 150 | 567.75
| 6-75-355-5-4 |  |  |  |  | 30 |  | 0 | [6 empty] | 120 | 167.1 | 75.1156 | 149 | 563.965 | 120 | 161.9 | 72.2244 | 150 | 567.75 | 120 | 155.9 | 68.8884 | 151 | 571.535 | 120 | 150.9 | 66.1084 | 152 | 575.32 | 120 | 77.4 | 25.2424 | 150 | 567.75
| 6-75-355-5-5 |  |  |  |  | 40 |  | 0.3 | -0.52288 | [5 empty] | 150 | 167.2 | 75.1712 | 151 | 571.535 | 150 | 161.9 | 72.2244 | 150 | 567.75 | 150 | 156 | 68.944 | 150 | 567.75 | 150 | 150.8 | 66.0528 | 153 | 579.105 | 150 | 77.3 | 25.1868 | 149 | 563.965
| 6-75-355-5-6 |  |  |  |  | 50 |  | 0.8 | -0.09691 | [5 empty] | 180 | 167.1 | 75.1156 | 152 | 575.32 | 180 | 161.8 | 72.1688 | 151 | 571.535 | 180 | 156.1 | 68.9996 | 149 | 563.965 | 180 | 150.7 | 65.9972 | 149 | 563.965 | 180 | 77.3 | 25.1868 | 150 | 567.75
[15 empty] | 210 | 167.1 | 75.1156 | 152 | 575.32 | 210 | 161.9 | 72.2244 | 152 | 575.32 | 210 | 156.4 | 69.1664 | 151 | 571.535 | 210 | 150.6 | 65.9416 | 153 | 579.105 | 210 | 77.3 | 25.1868 | 149 | 563.965
Sample Date | Sample No. | Challenge Test No | Temperature (Deg.C) | Flow Rate (L/min) | Sample Port | Sample time (second) |  | MS2 Count (pfu/mL) | log (count) | Average | SD |  |  |  | 240 | 167 | 75.06 | 151 | 571.535 | 240 | 161.9 | 72.2244 | 151 | 571.535 | 240 | 156.3 | 69.1108 | 150 | 567.75 | 240 | 150.6 | 65.9416 | 152 | 575.32 | 240 | 77.2 | 25.1312 | 150 | 567.75
2015-04-22 | 7-72-355-5-1 | 7 | 72 | 355 | 5 | 0 |  | 6 | 0.77815 | 0.84937 | 0.19206 | 4.1142 | 0.32216 | 4.0949 | 270 | 166.9 | 75.0044 | 152 | 575.32 | 270 | 161.8 | 72.1688 | 151 | 571.535 | 270 | 156.4 | 69.1664 | 152 | 575.32 | 270 | 150.8 | 66.0528 | 152 | 575.32 | 270 | 77.2 | 25.1312 | 149 | 563.965
| 7-72-355-5-2 |  |  |  |  | 10 |  | 5 | 0.69897 | [5 empty] | 300 | 166.9 | 75.0044 | 151 | 571.535 | 300 | 161.7 | 72.1132 | 150 | 567.75 | 300 | 156.3 | 69.1108 | 151 | 571.535 | 300 | 150.9 | 66.1084 | 153 | 579.105 | 300 | 77.1 | 25.0756 | 150 | 567.75
| 7-72-355-5-3 |  |  |  |  | 20 |  | 8 | 0.90309 | [5 empty] | 330 | 166.9 | 75.0044 | 153 | 579.105 | 330 |  |  |  |  | 330 |  |  |  |  | 330 |  |  |  |  | 330
| 7-72-355-5-4 |  |  |  |  | 30 |  | 4 | 0.60206 | [5 empty] | 360 | 166.8 | 74.9488 | 152 | 575.32 | 360 |  |  |  |  | 360 |  |  |  |  | 360 |  |  |  |  | 360
| 7-72-355-5-5 |  |  |  |  | 40 |  | 10 | 1 | [5 empty] | 390 | 166.9 | 75.0044 | 151 | 571.535 | 390 |  |  |  |  | 390 |  |  |  |  | 390 |  |  |  |  | 390
| 7-72-355-5-6 |  |  |  |  | 50 |  | 13 | 1.1139 | [5 empty] | 420 | 167 | 75.06 | 152 | 575.32 | 420 |  |  |  |  | 420 |  |  |  |  | 420 |  |  |  |  | 420
[17 empty] | Average |  | Average |  |  | Average |  | Average |  |  | Average |  | Average |  |  | Average |  | Average |  |  | Average |  | Average
Sample Date | Sample No. | Challenge Test No | Temperature (Deg.C) | Flow Rate (L/min) | Sample Port | Sample time (second) |  | MS2 Count (pfu/mL) | log (count) | Average | SD | [5 empty] | 75.0674 |  | 572.5443 |  |  | 72.1637 |  | 571.535 |  |  | 69.0198 |  | 569.4705 |  |  | 66.0629 |  | 573.5995 |  |  | 25.1969 |  | 569.4705
2015-04-22 | 8-69-355-5-1 | 8 | 69 | 355 | 5 | 0 |  | 1880 | 3.2742 | 3.3361 | 0.033715 | 1.6275 | 0.16381 | 1.6424 | Feed pump setting (Hz) | not recorded |  |  |  | Feed pump setting (Hz) | not recorded |  |  |  | Feed pump setting (Hz) |  |  |  |  | Feed pump setting (Hz) | 22 |  |  |  | Feed pump setting (Hz) | 21
| 8-69-355-5-2 |  |  |  |  | 10 |  | 2120 | 3.3263 | [5 empty] | Effluent Pump position (%) | nor recorded |  |  |  | Effluent Pump position (%) | nor recorded |  |  |  | Effluent Pump position (%) |  |  |  |  | Effluent Pump position (%) | 46 |  |  |  | Effluent Pump position (%) | 45
| 8-69-355-5-3 |  |  |  |  | 20 |  | 2260 | 3.3541
| 8-69-355-5-4 |  |  |  |  | 30 |  | 2170 | 3.3365 | [29 empty] | Overall Average Flow
| 8-69-355-5-5 |  |  |  |  | 40 |  | 2290 | 3.3598 | [29 empty] | 571.324
| 8-69-355-5-6 |  |  |  |  | 50 |  | 2320 | 3.3655 | [5 empty] | F to C | (F-32) x 0.556
[15 empty] | C to F | (C x 1,8) + 32
Sample Date | Sample No. | Challenge Test No | Temperature (Deg.C) | Flow Rate (L/min) | Sample Port | Sample time (second) |  | MS2 Count (pfu/mL) | log (count) | Average | SD |  |  |  | GPM to L/min | GPM x 3.785
2015-04-22 | 9-66-355-5-1 | 9 | 66 | 355 | 5 | 0 |  | 28000 | 4.4472 | 4.3584 | 0.17903 | 0.60516 | 0.30913 | 0.5933
| 9-66-355-5-2 |  |  |  |  | 10 |  | 25000 | 4.3979
| 9-66-355-5-3 |  |  |  |  | 20 |  | 38000 | 4.5798
| 9-66-355-5-4 |  |  |  |  | 30 |  | 23000 | 4.3617
| 9-66-355-5-5 |  |  |  |  | 40 |  | 21000 | 4.3222
| 9-66-355-5-6 |  |  |  |  | 50 |  | 11000 | 4.0414
Sample Date | Sample No. | Challenge Test No | Temperature (Deg.C) | Flow Rate (L/min) | Sample Port | Sample time (second) |  | MS2 Count (pfu/mL) | log (count) | Average | SD
2015-04-22 | 10-amb-355-5-1 | 10 | ambient | 355 | 5 | 0 |  | 139000 | 5.143 | 4.9635 | 0.1301 |  |  | 4.9795
| 10-amb-355-5-2 |  |  |  |  | 10 |  | 109000 | 5.0374
| 10-amb-355-5-3 |  |  |  |  | 20 | Triplicate assay | 104333.3333 | 5.0184
| 10-amb-355-5-4 |  |  |  |  | 30 |  | 79000 | 4.8976
| 10-amb-355-5-5 |  |  |  |  | 40 |  | 59000 | 4.7709
| 10-amb-355-5-6 |  |  |  |  | 50 |  | 82000 | 4.9138
Average SD
0.3066
Note on H5: Peter Sanciolo: Start of timing after 3 x HRT has passed aftyer start of injection of MS2.
Note on H13: Peter Sanciolo: Start of timing after 3 x HRT has passed aftyer start of injection of MS2.
Note on H21: Peter Sanciolo: Start of timing after 3 x HRT has passed aftyer start of injection of MS2.
Note on H29: Peter Sanciolo: Start of timing after 3 x HRT has passed aftyer start of injection of MS2.
Note on H37: Peter Sanciolo: Start of timing after 3 x HRT has passed aftyer start of injection of MS2.

## Microbial Challenge MS2+E.coli
Low temp. MS2 Challenge test with assay of native E.Coli | [19 empty] | Test Conditions
[20 empty] | Time (sec) | Temperaure (F) (=68C) | Temperature (C) | Flow (GPM) | Flow (L/min) | Time (sec) | Temperaure (F) (=64C) | Temperature (C) | Flow (GPM) | Flow (L/min) | Time (sec) | Temperaure (F) (=60C) | Temperature (C) | Flow (GPM) | Flow (L/min) | Time (sec) | Temperaure (F) (=57C) | Temperature (C) | Flow (GPM) | Flow (L/min)
Sample Date | Sample No. | Challenge Test No | Temperature (Deg.C) | Flow Rate (L/min) | Sample Port | Sample time after 14.5 minutes(second) |  | MS2 counts | log (count) | Average (Log (count)) | SD (log(count)) | LRV | SD (LRV) | E.coli Count (orgs/mL) | log (count) | Average (Log (count)) | SD (log(count)) | LRV | SD (LRV) | 0 | 154.2 | 67.9432 | 287 | 1086.295 | 0 | 147.1 | 63.9956 | 290 | 1097.65 | 0 | 140 | 60.048 | 292 | 1105.22 | 0 | 134.9 | 57.2124 | 300 | 1135.5
2015-04-24 | 11-57-1065-1-1 | 11 | 57 | 1065 | 1 | 0 |  | 30000 | 4.4771 | 4.4546 | 0.031522 | -0.00020901 | 0.054231 | 57000 | 4.7559 | 4.9576 | 0.20368 | 0.40681 | 0.26559 | 30 | 154.3 | 67.9988 | 289 | 1093.865 | 30 | 147.3 | 64.1068 | 296 | 1120.36 | 30 | 139.8 | 59.9368 | 289 | 1093.865 | 30 | 134.9 | 57.2124 | 301 | 1139.285
| 11-57-1065-1-2 |  |  |  |  | 20 |  | 26500 | 4.4232 |  |  |  |  | 63000 | 4.7993 |  |  |  |  | 60 | 154.3 | 67.9988 | 290 | 1097.65 | 60 | 147.3 | 64.1068 | 293 | 1109.005 | 60 | 140 | 60.048 | 296 | 1120.36 | 60 | 135 | 57.268 | 292 | 1105.22
| 11-57-1065-1-3 |  |  |  |  | 40 |  | 28500 | 4.4548 |  |  |  |  | 69000 | 4.8388 |  |  |  |  | 90 | 154.3 | 67.9988 | 292 | 1105.22 | 90 | 147.4 | 64.1624 | 300 | 1135.5 | 90 | 140 | 60.048 | 287 | 1086.295 | 90 | 134.9 | 57.2124 | 300 | 1135.5
| 11-57-1065-1-4 |  |  |  |  | 60 |  | 28400 | 4.4533 |  |  |  |  | 130000 | 5.1139 |  |  |  |  | 120 | 154.5 | 68.11 | 288 | 1090.08 | 120 | 147.5 | 64.218 | 285 | 1078.725 | 120 | 140.1 | 60.1036 | 291 | 1101.435 | 120 | 134.8 | 57.1568 | 294 | 1112.79
| 11-57-1065-1-5 |  |  |  |  | 80 |  | 26200 | 4.4183 |  |  |  |  | 190000 | 5.2788 |  |  |  |  | 150 | 154.6 | 68.1656 | 293 | 1109.005 | 150 | 147.3 | 64.1068 | 288 | 1090.08 | 150 | 140.2 | 60.1592 | 293 | 1109.005 | 150 | 134.8 | 57.1568 | 299 | 1131.715
| 11-57-1065-1-6 |  |  |  |  | 100 |  | 31700 | 4.5011 |  |  |  |  | 91000 | 4.959 |  |  |  |  | 180 | 154.5 | 68.11 | 286 | 1082.51 | 180 | 147.3 | 64.1068 | 289 | 1093.865 | 180 | 140.1 | 60.1036 | 294 | 1112.79 | 180 | 134.8 | 57.1568 | 297 | 1124.145
2015-04-24 | 11-57-1065-6-1 | 11 | 57 | 1065 | 6 | 0 |  | 27700 | 4.4425 | 4.4549 | 0.022709 |  |  | 37000 | 4.5682 | 4.5508 | 0.061911 |  |  | 210 | 154.6 | 68.1656 | 291 | 1101.435 | 210 | 147.2 | 64.0512 | 291 | 1101.435 | 210 | 140.1 | 60.1036 | 288 | 1090.08 | 210 | 134.6 | 57.0456 | 292 | 1105.22
| 11-57-1065-6-2 |  |  |  |  | 20 |  | 28500 | 4.4548 |  |  |  |  | 40000 | 4.6021 |  |  |  |  | 240 | 154.5 | 68.11 | 287 | 1086.295 | 240 | 147.2 | 64.0512 | 292 | 1105.22 | 240 | 140 | 60.048 | 293 | 1109.005 | 240 | 134.7 | 57.1012 | 291 | 1101.435
| 11-57-1065-6-3 |  |  |  |  | 40 | Triplicate assay | 30800 | 4.4886 |  |  |  |  | 39000 | 4.5911 |  |  |  |  | 270 | 154.4 | 68.0544 | 289 | 1093.865 | 270 | 147.3 | 64.1068 | 295 | 1116.575 | 270 | 139.9 | 59.9924 | 297 | 1124.145 | 270 | 134.6 | 57.0456 | 294 | 1112.79
| 11-57-1065-6-4 |  |  |  |  | 60 |  | 26400 | 4.4216 |  |  |  |  | 37000 | 4.5682 |  |  |  |  | 300 | 154.3 | 67.9988 | 286 | 1082.51 | 300 | 147.5 | 64.218 | 293 | 1109.005 | 300 | 140 | 60.048 | 295 | 1116.575 | 300 | 134.7 | 57.1012 | 295 | 1116.575
| 11-57-1065-6-5 |  |  |  |  | 80 |  | 29400 | 4.4683 |  |  |  |  | 35000 | 4.5441 |  |  |  |  | 330 | 154.3 | 67.9988 | 293 | 1109.005 | 330 | 147.4 | 64.1624 | 291 | 1101.435 | 330 | 140.1 | 60.1036 | 296 | 1120.36 | 330 | 134.8 | 57.1568 | 296 | 1120.36
| 11-57-1065-6-6 |  |  |  |  | 100 |  | 28400 | 4.4533 |  |  |  |  | 27000 | 4.4314 |  |  |  |  | 360 | 154.4 | 68.0544 | 292 | 1105.22 | 360 | 147.4 | 64.1624 | 295 | 1116.575 | 360 | 140.1 | 60.1036 | 291 | 1101.435 | 360 | 134.9 | 57.2124 | 299 | 1131.715
[20 empty] | 390 | 154.5 | 68.11 | 288 | 1090.08 | 390 | 147.3 | 64.1068 | 289 | 1093.865 | 390 | 140.3 | 60.2148 | 302 | 1143.07 | 390 | 134.8 | 57.1568 | 300 | 1135.5
Sample Date | Sample No. | Challenge Test No | Temperature (Deg.C) | Flow Rate (L/min) | Sample Port | Sample time (second) | [7 empty] | E.coli Count (orgs/mL) | [5 empty] | 420 | 154.6 | 68.1656 | 293 | 1109.005 | 420 | 147.4 | 64.1624 | 295 | 1116.575 | 420 | 140.4 | 60.2704 | 296 | 1120.36 | 420 | 134.7 | 57.1012 | 291 | 1101.435
2015-04-24 | 12-60-1065-1-1 | 12 | 60 | 1065 | 1 | 0 |  | 28600 | 4.4564 | 4.4095 | 0.026797 | -0.033335 | 0.093779 | 87000 | 4.9395 | 4.9279 | 0.10639 | 0.78397 | 0.15473 | 450 | 154.7 | 68.2212 | 291 | 1101.435 | 450 | 147.2 | 64.0512 | 298 | 1127.93 | 450 | 140.4 | 60.2704 | 301 | 1139.285 | 450 | 134.6 | 57.0456 | 300 | 1135.5
| 12-60-1065-1-2 |  |  |  |  | 20 |  | 25500 | 4.4065 |  |  |  |  | 60000 | 4.7782 |  |  |  |  | 480 | 154.7 | 68.2212 | 289 | 1093.865 | 480 | 147.2 | 64.0512 | 289 | 1093.865 | 480 | 140.4 | 60.2704 | 300 | 1135.5 | 480 | 134.7 | 57.1012 | 305 | 1154.425
| 12-60-1065-1-3 |  |  |  |  | 40 |  | 25800 | 4.4116 |  |  |  |  | 120000 | 5.0792 |  |  |  |  | 510 | 154.5 | 68.11 | 294 | 1112.79 | 510 | 147.2 | 64.0512 | 292 | 1105.22 | 510 | 140.2 | 60.1592 | 293 | 1109.005 | 510 | 134.6 | 57.0456 | 290 | 1097.65
| 12-60-1065-1-4 |  |  |  |  | 60 |  | 24700 | 4.3927 |  |  |  |  | 71000 | 4.8513 |  |  |  |  | 540 | 154.4 | 68.0544 | 286 | 1082.51 | 540 | 147 | 63.94 | 296 | 1120.36 | 540 | 140.1 | 60.1036 | 287 | 1086.295 | 540 | 134.6 | 57.0456 | 299 | 1131.715
| 12-60-1065-1-5 |  |  |  |  | 80 |  | 25900 | 4.4133 |  |  |  |  | 83000 | 4.9191 |  |  |  |  | 570 | 154.4 | 68.0544 | 289 | 1093.865 | 570 | 147 | 63.94 | 298 | 1127.93 | 570 | 140 | 60.048 | 293 | 1109.005 | 570 | 134.7 | 57.1012 | 289 | 1093.865
| 12-60-1065-1-6 |  |  |  |  | 100 |  | 23800 | 4.3766 |  |  |  |  | 100000 | 5 |  |  |  |  | 600 | 154.5 | 68.11 | 293 | 1109.005 | 600 | 147 | 63.94 | 293 | 1109.005 | 600 | 140.1 | 60.1036 | 291 | 1101.435 | 600 | 134.7 | 57.1012 | 286 | 1082.51
2015-04-24 | 12-60-1065-6-1 | 12 | 60 | 1065 | 6 | 0 |  | 35000 | 4.5441 | 4.4429 | 0.066982 |  |  | 13000 | 4.1139 | 4.1439 | 0.048337 |  |  | 630 | 154.4 | 68.0544 | 295 | 1116.575 | 630 | 147.1 | 63.9956 | 283 | 1071.155 | 630 | 140.1 | 60.1036 | 296 | 1120.36 | 630 | 134.6 | 57.0456 | 290 | 1097.65
| 12-60-1065-6-2 |  |  |  |  | 20 |  | 26000 | 4.415 |  |  |  |  | 15000 | 4.1761 |  |  |  |  | 660 | 154.6 | 68.1656 | 295 | 1116.575 | 660 | 147.1 | 63.9956 | 297 | 1124.145 | 660 | 140 | 60.048 | 301 | 1139.285 | 660 | 134.6 | 57.0456 | 290 | 1097.65
| 12-60-1065-6-3 |  |  |  |  | 40 |  | 22000 | 4.3424 |  |  |  |  | 16000 | 4.2041 |  |  |  |  | 690 | 154.6 | 68.1656 | 294 | 1112.79 | 690 | 147.2 | 64.0512 | 293 | 1109.005 | 690 | 139.8 | 59.9368 | 300 | 1135.5 | 690 | 134.6 | 57.0456 | 297 | 1124.145
| 12-60-1065-6-4 |  |  |  |  | 60 |  | 27000 | 4.4314 |  |  |  |  | 13000 | 4.1139 |  |  |  |  | 720 | 154.4 | 68.0544 | 288 | 1090.08 | 720 | 147.3 | 64.1068 | 291 | 1101.435 | 720 | 139.7 | 59.8812 | 296 | 1120.36 | 720 | 134.4 | 56.9344 | 298 | 1127.93
| 12-60-1065-6-5 |  |  |  |  | 80 |  | 28000 | 4.4472 |  |  |  |  | 15000 | 4.1761 |  |  |  |  | 750 | 154.3 | 67.9988 | 296 | 1120.36 | 750 | 147.2 | 64.0512 | 292 | 1105.22 | 750 | 139.7 | 59.8812 | 286 | 1082.51 | 750 | 134.4 | 56.9344 | 303 | 1146.855
| 12-60-1065-6-6 |  |  |  |  | 100 |  | 30000 | 4.4771 |  |  |  |  | 12000 | 4.0792 |  |  |  |  | 780 | 154.3 | 67.9988 | 292 | 1105.22 | 780 | 147.3 | 64.1068 | 290 | 1097.65 | 780 | 139.7 | 59.8812 | 301 | 1139.285 | 780 | 134.5 | 56.99 | 301 | 1139.285
[20 empty] | 810 | 154.3 | 67.9988 | 300 | 1135.5 | 810 | 147.5 | 64.218 | 295 | 1116.575 | 810 | 139.8 | 59.9368 | 305 | 1154.425 | 810 | 134.6 | 57.0456 | 293 | 1109.005
Sample Date | Sample No. | Challenge Test No | Temperature (Deg.C) | Flow Rate (L/min) | Sample Port | Sample time (second) | [7 empty] | E.coli Count (orgs/mL) | [5 empty] | 840 | 154.2 | 67.9432 | 296 | 1120.36 | 840 | 147.5 | 64.218 | 289 | 1093.865 | 840 | 140 | 60.048 | 296 | 1120.36 | 840 | 134.7 | 57.1012 | 289 | 1093.865
2015-04-24 | 13-63-1065-1-1 | 13 | 64 | 1065 | 1 | 0 |  | 12400 | 4.0934 | 4.161 | 0.044262 | -0.016355 | 0.085933 | 61000 | 4.7853 | 4.7474 | 0.046474 | 1.4796 | 0.16395 | 870 | 154.3 | 67.9988 | 286 | 1082.51 | 870 | 147.4 | 64.1624 | 287 | 1086.295 | 870 | 140 | 60.048 | 295 | 1116.575 | 870 | 134.7 | 57.1012 | 292 | 1105.22
| 13-63-1065-1-2 |  |  |  |  | 20 |  | 13900 | 4.143 |  |  |  |  | 48000 | 4.6812 |  |  |  |  | 900 | 154.3 | 67.9988 | 290 | 1097.65 | 900 | 147.5 | 64.218 | 295 | 1116.575 | 900 | 140 | 60.048 | 301 | 1139.285 | 900 | 134.6 | 57.0456 | 278 | 1052.23
| 13-63-1065-1-3 |  |  |  |  | 40 |  | 15500 | 4.1903 |  |  |  |  | 62000 | 4.7924 |  |  |  |  | 930 | 154.3 | 67.9988 | 291 | 1101.435 | 930 | 147.4 | 64.1624 | 291 | 1101.435 | 930 | 140.1 | 60.1036 | 292 | 1105.22 | 930 | 134.7 | 57.1012 | 294 | 1112.79
| 13-63-1065-1-4 |  |  |  |  | 60 |  | 15000 | 4.1761 |  |  |  |  | 52000 | 4.716 |  |  |  |  | 960 | 154.2 | 67.9432 | 289 | 1093.865 | 960 | 147.5 | 64.218 | 294 | 1112.79 | 960 | 140.2 | 60.1592 | 294 | 1112.79 | 960 | 134.5 | 56.99 | 288 | 1090.08
| 13-63-1065-1-5 |  |  |  |  | 80 |  | 13900 | 4.143 |  |  |  |  | 61000 | 4.7853 |  |  |  |  | 990 | 154.2 | 67.9432 | 295 | 1116.575 | 990 | 147.3 | 64.1068 | 284 | 1074.94 | 990 | 140.1 | 60.1036 | 300 | 1135.5 | 990 | 134.4 | 56.9344 | 295 | 1116.575
| 13-63-1065-1-6 |  |  |  |  | 100 |  | 16600 | 4.2201 |  |  |  |  | 53000 | 4.7243 |  |  |  |  | 1020 | 154.4 | 68.0544 | 291 | 1101.435 | 1020 |  |  |  |  | 1020 | 139.8 | 59.9368 | 301 | 1139.285 | 1020
2015-04-24 | 13-63-1065-6-1 | 13 | 64 | 1065 | 6 | 0 |  | 16300 | 4.2122 | 4.1774 | 0.041671 |  |  | 1600 | 3.2041 | 3.2679 | 0.11747 |  |  | 1050 | 154.6 | 68.1656 | 290 | 1097.65 | 1050 |  |  |  |  | 1050 |  |  |  |  | 1050
| 13-63-1065-6-2 |  |  |  |  | 20 |  | 15200 | 4.1818 |  |  |  |  | 1600 | 3.2041 |  |  |  |  | 1080 | 154.6 | 68.1656 | 300 | 1135.5 | 1080 |  |  |  |  | 1080 |  |  |  |  | 1080
| 13-63-1065-6-3 |  |  |  |  | 40 |  | 16100 | 4.2068 |  |  |  |  | 1700 | 3.2304 | [6 empty] | Average |  | Average |  |  | Average |  | Average |  |  | Average |  | Average |  |  | Average |  | Average
| 13-63-1065-6-4 |  |  |  |  | 60 |  | 16100 | 4.2068 |  |  |  |  | 1500 | 3.1761 | [6 empty] | 68.0649 |  | 1102.1511 |  |  | 64.1003 |  | 1105.3313 |  |  | 60.0687 |  | 1117.0076 |  |  | 57.0898 |  | 1115.2391
| 13-63-1065-6-5 |  |  |  |  | 80 |  | 14100 | 4.1492 |  |  |  |  | 3100 | 3.4914
| 13-63-1065-6-6 |  |  |  |  | 100 |  | 12800 | 4.1072 |  |  |  |  | 2000 | 3.301
[20 empty] | Feed pump setting (Hz) | not recorded |  |  |  | Feed pump setting (Hz) | 35 |  |  |  | Feed pump setting (Hz) | 35 |  |  |  | Feed pump setting (Hz) | 35
Sample Date | Sample No. | Challenge Test No | Temperature (Deg.C) | Flow Rate (L/min) | Sample Port | Sample time (second) | [7 empty] | E.coli Count (orgs/mL) | [5 empty] | Effluent Pump position (%) | nor recorded |  |  |  | Effluent Pump position (%) | nor recorded |  |  |  | Effluent Pump position (%) |  |  |  |  | Effluent Pump position (%) |  |  |  | Overall Average Flow
2015-04-24 | 14-66-1065-1-1 | 14 | 68 | 1065 | 1 | 0 |  | 14100 | 4.1492 | 4.1351 | 0.034259 | 0.76112 | 0.21608 | 68000 | 4.8325 | 4.765 | 0.060119 | 2.886 | 0.33261 | [19 empty] | 1187.9458
| 14-66-1065-1-2 |  |  |  |  | 20 |  | 12000 | 4.0792 |  |  |  |  | 63000 | 4.7993
| 14-66-1065-1-3 |  |  |  |  | 40 |  | 13600 | 4.1335 |  |  |  |  | 65000 | 4.8129
| 14-66-1065-1-4 |  |  |  |  | 60 |  | 14600 | 4.1644 |  |  |  |  | 57000 | 4.7559
| 14-66-1065-1-5 |  |  |  |  | 80 |  | 13000 | 4.1139 |  |  |  |  | 50000 | 4.699
| 14-66-1065-1-6 |  |  |  |  | 100 |  | 14800 | 4.1703 |  |  |  |  | 49000 | 4.6902
2015-04-24 | 14-66-1065-6-1 | 14 | 68 | 1065 | 6 | 0 |  | 1400 | 3.1461 | 3.374 | 0.18182 |  |  | 88 | 1.9445 | 1.879 | 0.27249
| 14-66-1065-6-2 |  |  |  |  | 20 |  | 2200 | 3.3424 |  |  |  |  | 120 | 2.0792
| 14-66-1065-6-3 |  |  |  |  | 40 |  | 1700 | 3.2304 |  |  |  |  | 22 | 1.3424
| 14-66-1065-6-4 |  |  |  |  | 60 |  | 3100 | 3.4914 |  |  |  |  | 75 | 1.8751
| 14-66-1065-6-5 |  |  |  |  | 80 |  | 4500 | 3.6532 |  |  |  |  | 98 | 1.9912
| 14-66-1065-6-6 |  |  |  |  | 100 |  | 2400 | 3.3802 |  |  |  |  | 110 | 2.0414
[13 empty] | Average SD | [5 empty] | Average SD
[13 empty] | 0.11251 | [5 empty] | 0.22922

## Microbial Challenge HF(1)
High Flow Challenge Test 1 | [13 empty] | Paul's
[14 empty] | Calculation | Test Conditions
Sample Date | Sample No. | Challenge Test No | Temperature (Deg.C) | Flow Rate (L/min) | Sample Port | Sample time (second) |  | MS2 count (pfu/mL) | log (count) | Average (Log (count)) | SD (log(count)) | LRV | SD (LRV) | LRV | Time (sec) | Temperaure (F) (=75C) | Temperature (C) | Flow (GPM) | Flow (L/min) | Time (sec) | Temperaure (F) (=72C) | Temperature (C) | Flow (GPM) | Flow (L/min) | Time (sec) | Temperaure (F) (=69C) | Temperature (C) | Flow (GPM) | Flow (L/min) | Time (sec) | Temperaure (F) (=66C) | Temperature (C) | Flow (GPM) | Flow (L/min) | Time (sec) | Temperaure (F) (ambient) | Temperature (C) | Flow (GPM) | Flow (L/min)
2015-04-24 | 1-75-1065-5-1 | 1 | 75 | 1065 | 5 | 0 |  | 0.3 | -0.52288 | -0.21217 | 0.37591 | 4.233 | 0.47566 | 4.1143 | 0 | 166.9 | 75.0044 | 290 | 1097.65 | 0 | 161.7 | 72.1132 | 292 | 1105.22 | 0 | 156.2 | 69.0552 | 293 | 1109.005 | 0 | 150.8 | 66.0528 | 283 | 1071.155 | 0 | 84 | 28.912 | 286 | 1082.51
| 1-75-1065-5-2 |  |  |  |  | 10 |  | 1 | 0 | [5 empty] | 30 | 166.9 | 75.0044 | 288 | 1090.08 | 30 | 161.6 | 72.0576 | 292 | 1105.22 | 30 | 156.1 | 68.9996 | 289 | 1093.865 | 30 | 150.8 | 66.0528 | 291 | 1101.435 | 30 | 83.9 | 28.8564 | 284 | 1074.94
| 1-75-1065-5-3 |  |  |  |  | 20 |  | 1 | 0 | [5 empty] | 60 | 166.8 | 74.9488 | 284 | 1074.94 | 60 | 161.7 | 72.1132 | 295 | 1116.575 | 60 | 156.2 | 69.0552 | 291 | 1101.435 | 60 | 150.9 | 66.1084 | 286 | 1082.51 | 60 | 83.9 | 28.8564 | 287 | 1086.295
| 1-75-1065-5-4 |  |  |  |  | 30 |  | 0.2 | -0.69897 | [5 empty] | 90 | 166.8 | 74.9488 | 287 | 1086.295 | 90 | 161.7 | 72.1132 | 291 | 1101.435 | 90 | 156.2 | 69.0552 | 293 | 1109.005 | 90 | 150.7 | 65.9972 | 284 | 1074.94 | 90 | 83.5 | 28.634 | 285 | 1078.725
| 1-75-1065-5-5 |  |  |  |  | 40 |  | 2 | 0.30103 | [5 empty] | 120 | 166.7 | 74.8932 | 286 | 1082.51 | 120 | 161.7 | 72.1132 | 293 | 1109.005 | 120 | 156.1 | 68.9996 | 293 | 1109.005 | 120 | 150.8 | 66.0528 | 291 | 1101.435 | 120 | 83.4 | 28.5784 | 287 | 1086.295
| 1-75-1065-5-6 |  |  |  |  | 50 |  | 0.44444 | -0.35218 | [5 empty] | 150 | 166.7 | 74.8932 | 292 | 1105.22 | 150 | 161.7 | 72.1132 | 294 | 1112.79 | 150 | 156.3 | 69.1108 | 287 | 1086.295 | 150 | 150.8 | 66.0528 | 290 | 1097.65 | 150 | 83.3 | 28.5228 | 287 | 1086.295
[15 empty] | 180 | 166.8 | 74.9488 | 284 | 1074.94 | 180 | 161.6 | 72.0576 | 291 | 1101.435 | 180 | 156.1 | 68.9996 | 284 | 1074.94 | 180 | 150.9 | 66.1084 | 287 | 1086.295 | 180 | 83.3 | 28.5228 | 286 | 1082.51
Sample Date | Sample No. | Challenge Test No | Temperature (Deg.C) | Flow Rate (L/min) | Sample Port | Sample time (second) |  | MS2 count (pfu/mL) | log (count) | Average | SD |  |  |  | 210 | 166.9 | 75.0044 | 294 | 1112.79 | 210 | 161.5 | 72.002 | 293 | 1109.005 | 210 | 156.3 | 69.1108 | 287 | 1086.295 | 210 | 150.9 | 66.1084 | 285 | 1078.725 | 210 | 83.1 | 28.4116 | 284 | 1074.94
2015-04-24 | 2-72-1065-5-1 | 2 | 72 | 1065 | 5 | 0 |  | 79 | 1.8976 | 1.8137 | 0.10516 | 2.2072 | 0.20492 | 2.2064 | 240 | 167 | 75.06 | 294 | 1112.79 | 240 |  |  |  |  | 240 |  |  |  |  | 240 |  |  |  |  | 240
| 2-72-1065-5-2 |  |  |  |  | 10 |  | 80 | 1.9031 | [5 empty] | 270 |  |  |  |  | 270 |  |  |  |  | 270 |  |  |  |  | 270 |  |  |  |  | 270
| 2-72-1065-5-3 |  |  |  |  | 20 |  | 65 | 1.8129 | [5 empty] | 300 |  | Average |  | Average | 300 |  | Average |  | Average | 300 |  | Average |  | Average | 300 |  | Average |  | Average | 300 |  | Average |  | Average
| 2-72-1065-5-4 |  |  |  |  | 30 |  | 50 | 1.699 | [5 empty] | 330 |  | 74.9673 |  | 1093.0239 | 330 |  | 72.0854 |  | 1107.5856 | 330 |  | 69.0483 |  | 1096.2306 | 330 |  | 66.0667 |  | 1086.7681 | 330 |  | 28.6618 |  | 1081.5638
| 2-72-1065-5-5 |  |  |  |  | 40 |  | 79 | 1.8976 | [5 empty] | 360 |  | SD |  | SD | 360 |  | SD |  | SD | 360 |  | SD |  | SD | 360 |  | SD |  | SD | 360 |  | SD |  | SD
| 2-72-1065-5-6 |  |  |  |  | 50 |  | 47 | 1.6721 | [5 empty] | 390 |  | 0.0556 |  | 14.8748 | 390 |  | 0.04203 |  | 5.3288 | 390 |  | 0.046399 |  | 12.9447 | 390 |  | 0.039315 |  | 12.0438 | 390 |  | 0.18796 |  | 4.8514
[15 empty] | 420 |  |  |  |  | 420 |  |  |  |  | 420 |  |  |  |  | 420 |  |  |  |  | 420
Sample Date | Sample No. | Challenge Test No | Temperature (Deg.C) | Flow Rate (L/min) | Sample Port | Sample time (second) |  | MS2 count (pfu/mL) | log (count) | Average | SD | [27 empty] | 1093.0344
2015-04-24 | 3-69-1065-5-1 | 3 | 69 | 1065 | 5 | 0 |  | 2030 | 3.3075 | 3.2783 | 0.036093 | 0.74256 | 0.13585 | 0.75077 | Feed pump setting (Hz) | not recorded |  |  |  | Feed pump setting (Hz) | not recorded |  |  |  | Feed pump setting (Hz) |  |  |  |  | Feed pump setting (Hz) | 22 |  |  |  | Feed pump setting (Hz) | 21
| 3-69-1065-5-2 |  |  |  |  | 10 |  | 1610 | 3.2068 | [5 empty] | Effluent Pump position (%) | nor recorded |  |  |  | Effluent Pump position (%) | nor recorded |  |  |  | Effluent Pump position (%) |  |  |  |  | Effluent Pump position (%) | 46 |  |  |  | Effluent Pump position (%) | 45
| 3-69-1065-5-3 |  |  |  |  | 20 |  | 1930 | 3.2856
| 3-69-1065-5-4 |  |  |  |  | 30 |  | 1920 | 3.2833
| 3-69-1065-5-5 |  |  |  |  | 40 |  | 1980 | 3.2967
| 3-69-1065-5-6 |  |  |  |  | 50 |  | 1950 | 3.29
Sample Date | Sample No. | Challenge Test No | Temperature (Deg.C) | Flow Rate (L/min) | Sample Port | Sample time (second) |  | MS2 count (pfu/mL) | log (count) | Average | SD
2015-04-24 | 4-66-1065-5-1 | 4 | 66 | 1065 | 5 | 0 |  | 2800 | 3.4472 | 3.216 | 0.15362 | 0.80492 | 0.25337 | 0.7914
| 4-66-1065-5-2 |  |  |  |  | 10 |  | 2100 | 3.3222
| 4-66-1065-5-3 |  |  |  |  | 20 |  | 1500 | 3.1761
| 4-66-1065-5-4 |  |  |  |  | 30 |  | 1600 | 3.2041
| 4-66-1065-5-5 |  |  |  |  | 40 |  | 1000 | 3
| 4-66-1065-5-6 |  |  |  |  | 50 |  | 1400 | 3.1461
Sample Date | Sample No. | Challenge Test No | Temperature (Deg.C) | Flow Rate (L/min) | Sample Port | Sample time (second) |  | MS2 count (pfu/mL) | log (count) | Average | SD |  |  | LV
2015-04-24 | 5-amb-1065-5-1 | 5 | ambient | 1065 | 5 | 0 |  | 7300 | 3.8633 | 4.0209 | 0.099758 |  |  | 4.0303
| 5-amb-1065-5-2 |  |  |  |  | 10 |  | 10900 | 4.0374
| 5-amb-1065-5-3 |  |  |  |  | 20 | Triplicate assay | 11133 | 4.0466
| 5-amb-1065-5-4 |  |  |  |  | 30 |  | 9400 | 3.9731
| 5-amb-1065-5-5 |  |  |  |  | 40 |  | 10900 | 4.0374
| 5-amb-1065-5-6 |  |  |  |  | 50 |  | 14700 | 4.1673
Average SD
0.26745
27-05-15 results
[15 empty] | 75 | 5.2587
[15 empty] | 72 | 2.4481
[15 empty] | 69 | 0.8256
Note on H5: Peter Sanciolo: Start of timing after 3 x HRT has passed aftyer start of injection of MS2.
Note on H13: Peter Sanciolo: Start of timing after 3 x HRT has passed aftyer start of injection of MS2.
Note on H21: Peter Sanciolo: Start of timing after 3 x HRT has passed aftyer start of injection of MS2.
Note on H29: Peter Sanciolo: Start of timing after 3 x HRT has passed aftyer start of injection of MS2.
Note on H37: Peter Sanciolo: Start of timing after 3 x HRT has passed aftyer start of injection of MS2.

## Microbial Challenge HF(2)
High Flow Challenge Test 2
Test Conditions
Sample Date | Sample No. | Challenge Test No | Temperature (Deg.C) | Flow Rate (L/min) | Sample Port | Sample time (second) |  | MS2 count (pfu/mL) | log (count) | Average (Log (count)) | SD (log(count)) | LRV | SD (LRV) | Time (sec) | Temperaure (F) (=75C) | Temperature (C) | Flow (GPM) | Flow (L/min) | Time (sec) | Temperaure (F) (=72C) | Temperature (C) | Flow (GPM) | Flow (L/min) | Time (sec) | Temperaure (F) (=69C) | Temperature (C) | Flow (GPM) | Flow (L/min) | Time (sec) | Temperaure (F) (=66C) | Temperature (C) | Flow (GPM) | Flow (L/min)
2015-05-27 | 15-75-1065-5-1 | 15 | 75 | 1065 | 5 | 0 |  | 1.7 | 0.23045 | 0.15051 | 0.1738 | 5.2834 | 0.20435 | 0 | 167.1 | 75.1156 | 277 | 1048.445 | 0 | 162.4 | 72.5024 | 287 | 1086.295 | 0 | 156.2 | 69.0552 | 286 | 1082.51 | 0 | 84.6 | 29.2456 | 281 | 1063.585
| 15-75-1065-5-2 |  |  |  |  | 30 |  | 1.3 | 0.11394 |  |  |  |  | 30 | 167.1 | 75.1156 | 281 | 1063.585 | 30 | 162.1 | 72.3356 | 286 | 1082.51 | 30 | 156.2 | 69.0552 | 287 | 1086.295 | 30 | 84.3 | 29.0788 | 278 | 1052.23
| 15-75-1065-5-3 |  |  |  |  | 60 |  | 2 | 0.30103 |  |  |  |  | 60 | 166.9 | 75.0044 | 275 | 1040.875 | 60 | 162 | 72.28 | 288 | 1090.08 | 60 | 155.9 | 68.8884 | 281 | 1063.585 | 60 | 84.2 | 29.0232 | 279 | 1056.015
| 15-75-1065-5-4 |  |  |  |  | 90 |  | 1 | 0 |  |  |  |  | 90 | 166.8 | 74.9488 | 288 | 1090.08 | 90 | 161.8 | 72.1688 | 281 | 1063.585 | 90 | 155.8 | 68.8328 | 284 | 1074.94 | 90 | 84.1 | 28.9676 | 278 | 1052.23
| 15-75-1065-5-5 |  |  |  |  | 120 |  | 1 | 0 |  |  |  |  | 120 | 166.6 | 74.8376 | 286 | 1082.51 | 120 | 161.9 | 72.2244 | 282 | 1067.37 | 120 | 157.7 | 69.8892 | 277 | 1048.445 | 120 | 83.9 | 28.8564 | 280 | 1059.8
| 15-75-1065-5-6 |  |  |  |  | 150 |  | 2 | 0.30103 |  |  |  |  | 150 | 166.7 | 74.8932 | 287 | 1086.295 | 150 | 161.8 | 72.1688 | 287 | 1086.295 | 150 | 155.8 | 68.8328 | 288 | 1090.08 | 150 | 83.8 | 28.8008 | 279 | 1056.015
| 15-75-1065-5-7 | [12 empty] | 180 | 166.7 | 74.8932 | 288 | 1090.08 | 180 | 161.7 | 72.1132 | 283 | 1071.155 | 180 | 156 | 68.944 | 281 | 1063.585 | 180 | 83.6 | 28.6896 | 277 | 1048.445
| 15-75-1065-5-8 | [7 empty] | log (count) | Average | SD |  |  | 210 | 166.4 | 74.7264 | 287 | 1086.295 | 210 | 161.8 | 72.1688 | 282 | 1067.37 | 210 | 156.3 | 69.1108 | 286 | 1082.51 | 210 | 83.3 | 28.5228 | 275 | 1040.875
2015-05-27 | 16-72-1065-5-1 | 16 | 72 | 1065 | 5 | 0 |  | 1370 | 3.1367 | 2.9642 | 0.16098 | 2.4697 | 0.19154 | 240 |  |  |  |  | 240 |  |  |  |  | 240 | 155.8 | 68.8328 | 289 | 1093.865 | 240 | 83 | 28.356 | 275 | 1040.875
| 16-72-1065-5-2 |  |  |  |  | 30 |  | 820 | 2.9138 |  |  |  |  | 270 |  |  |  |  | 270 |  |  |  |  | 270 |  |  |  |  | 270
| 16-72-1065-5-3 |  |  |  |  | 60 |  | 1240 | 3.0934 |  |  |  |  | 300 |  | Average |  | Average | 300 |  | Average |  | Average | 300 |  | Average |  | Average | 300 |  | Average |  | Average
| 16-72-1065-5-4 |  |  |  |  | 90 |  | 960 | 2.9823 |  |  |  |  | 330 |  | 74.9419 |  | 1073.5206 | 330 |  | 72.2453 |  | 1076.8325 | 330 |  | 69.049 |  | 1076.2017 | 330 |  | 28.8379 |  | 1052.23
| 16-72-1065-5-5 |  |  |  |  | 120 |  | 480 | 2.6812 |  |  |  |  | 360 |  | SD |  | SD | 360 |  | SD |  | SD | 360 |  | SD |  | SD | 360 |  | SD |  | SD
| 16-72-1065-5-6 |  |  |  |  | 150 |  | 950 | 2.9777 |  |  |  |  | 390 |  | 0.13436 |  | 19.8165 | 390 |  | 0.12587 |  | 10.5127 | 390 |  | 0.33296 |  | 14.9016 | 390 |  | 0.28077 |  | 7.803
| 16-69-1065-5-7 | [12 empty] | 420 |  |  |  |  | 420 |  |  |  |  | 420 |  |  |  |  | 420
| 16-69-1065-5-8 | [7 empty] | log (count) | Average | SD
2015-05-27 | 17-69-1065-5-1 | 17 | 69 | 1065 | 5 | 0 |  | 38000 | 4.5798 | 4.5912 | 0.14536 | 0.84273 | 0.17592
| 17-69-1065-5-2 |  |  |  |  | 30 |  | 51000 | 4.7076
| 17-69-1065-5-3 |  |  |  |  | 60 |  | 53000 | 4.7243
| 17-69-1065-5-4 |  |  |  |  | 90 |  | 38000 | 4.5798
| 17-69-1065-5-5 |  |  |  |  | 120 |  | 43000 | 4.6335
| 17-69-1065-5-6 |  |  |  |  | 150 |  | 21000 | 4.3222
17-69-1065-5-7
| 17-69-1065-5-8 | [7 empty] | log (count) | Average | SD
2015-05-27 | 18-amb-1065-5-1 | 18 | ambient | 1065 | 5 | 0 |  | 253000 | 5.4031 | 5.4339 | 0.030555
| 18-amb-1065-5-2 |  |  |  |  | 30 |  | 266000 | 5.4249
| 18-amb-1065-5-3 |  |  |  |  | 60 | Triplicate assay | 264000 | 5.4216
| 18-amb-1065-5-4 |  |  |  |  | 90 |  | 270000 | 5.4314
| 18-amb-1065-5-5 |  |  |  |  | 120 |  | 269000 | 5.4298
| 18-amb-1065-5-6 |  |  |  |  | 150 |  | 311000 | 5.4928
18-amb-1065-5-7
18-amb-1065-5-8
Average SD
0.1906
Note on H5: Peter Sanciolo: Start of timing after 3 x HRT has passed after start of injection of MS2.

## Microbial Challenge HF(3)
High Flow Challenge Test 3
Sample Date | Sample No. | Challenge Test No | Temperature (Deg.C) | Flow Rate (L/min) | Sample Port | Sample time (second) |  | MS2 count (pfu/mL) | log (count) | Average (Log (count)) | SD (log(count)) | LRV | SD (LRV)
2015-06-02 | 19-75-1065-5-1 | 19 | 75 | 1065 | 5 | 0 |  | 5 | 0.69897 | 0.42958 | 0.29872 | 4.9929 | 0.32199
| 19-75-1065-5-2 |  |  |  |  | 30 |  | 1.8 | 0.25527
| 19-75-1065-5-3 |  |  |  |  | 60 |  | 7 | 0.8451
| 19-75-1065-5-4 |  |  |  |  | 90 |  | 2 | 0.30103
| 19-75-1065-5-5 |  |  |  |  | 120 |  | 1.5 | 0.17609
| 19-75-1065-5-6 |  |  |  |  | 150 |  | 2 | 0.30103
| 19-75-1065-5-7 |  |  |  |  | 180
| 19-75-1065-5-8 |  |  |  |  | 210 |  |  | log (count) | Average | SD
2015-06-02 | 20-72-1065-5-1 | 20 | 72 | 1065 | 5 | 0 |  | 1110 | 3.0453 | 3.107 | 0.05009 | 2.3154 | 0.073354
| 20-72-1065-5-2 |  |  |  |  | 30 |  | 1210 | 3.0828
| 20-72-1065-5-3 |  |  |  |  | 60 |  | 1190 | 3.0755
| 20-72-1065-5-4 |  |  |  |  | 90 |  | 1380 | 3.1399
| 20-72-1065-5-5 |  |  |  |  | 120 |  | 1300 | 3.1139
| 20-72-1065-5-6 |  |  |  |  | 150 |  | 1530 | 3.1847
20-72-1065-5-7
| 20-72-1065-5-8 | [7 empty] | log (count) | Average | SD
2015-06-02 | 21-69-1065-5-1 | 21 | 69 | 1065 | 5 | 0 |  | 23500 | 4.3711 | 4.4034 | 0.029701 | 1.019 | 0.052965
| 21-69-1065-5-2 |  |  |  |  | 30 |  | 26700 | 4.4265
| 21-69-1065-5-3 |  |  |  |  | 60 |  | 23500 | 4.3711
| 21-69-1065-5-4 |  |  |  |  | 90 |  | 27200 | 4.4346
| 21-69-1065-5-5 |  |  |  |  | 120 |  | 24500 | 4.3892
| 21-69-1065-5-6 |  |  |  |  | 150 |  | 26800 | 4.4281
| 21-69-1065-5-7 |  |  |  |  | 180
| 21-69-1065-5-8 |  |  |  |  | 210 |  |  | log (count) | Average | SD
2015-06-02 | 22-amb-1065-5-1 | 22 | ambient | 1065 | 5 | 0 |  | 246000 | 5.3909 | 5.4225 | 0.023264
| 22-amb-1065-5-2 |  |  |  |  | 30 |  | 272000 | 5.4346
| 22-amb-1065-5-3 |  |  |  |  | 60 | Triplicate assay | 274000 | 5.4378
| 22-amb-1065-5-4 |  |  |  |  | 90 |  | 248000 | 5.3945
| 22-amb-1065-5-5 |  |  |  |  | 120 |  | 272000 | 5.4346
| 22-amb-1065-5-6 |  |  |  |  | 150 |  | 277000 | 5.4425
| 22-amb-1065-5-7 |  |  |  |  | 180
| 22-amb-1065-5-8 |  |  |  |  | 210
Average SD
0.14943
Note on H5: Peter Sanciolo: Start of timing after 3 x HRT has passed after start of injection of MS2.

## Microbial Challenge HF(4)
High Flow Challenge Test 4
Sample Date | Sample No. | Challenge Test No | Temperature (Deg.C) | Flow Rate (L/min) | Sample Port | Sample time (second) |  | MS2 count (pfu/mL) | log (count) | Average (Log (count)) | SD (log(count)) | LRV | SD (LRV)
2015-06-23 | 23-75-1065-5-1 | 23 | 75 | 1065 | 5 | 0 |  | 1.2 | 0.079181 | -0.020246 | 0.32522 | 5.4763 | 0.3466
| 23-75-1065-5-2 |  |  |  |  | 30 |  | 3 | 0.47712
| 23-75-1065-5-3 |  |  |  |  | 60 |  | 1 | 0
| 23-75-1065-5-4 |  |  |  |  | 90 |  | 0.7 | -0.1549
| 23-75-1065-5-5 |  |  |  |  | 120 |  | 0.3 | -0.52288
| 23-75-1065-5-6 |  |  |  |  | 150 |  | 1 | 0
2015-06-23 | 24-72-1065-5-1 | 24 | 72 | 1065 | 5 | 0
| 24-72-1065-5-2 |  |  |  |  | 30 |  |  | log (count) | Average | SD
| 24-72-1065-5-3 |  |  |  |  | 60 |  | 920 | 2.9638 | 3.0153 | 0.042366 | 2.4407 | 0.063738
| 24-72-1065-5-4 |  |  |  |  | 90 |  | 1150 | 3.0607
| 24-72-1065-5-5 |  |  |  |  | 120 |  | 950 | 2.9777
| 24-72-1065-5-6 |  |  |  |  | 150 |  | 1030 | 3.0128
2015-06-23 | 25-69-1065-5-1 | 25 | 69 | 1065 | 5 | 0 |  | 1020 | 3.0086
| 25-69-1065-5-2 |  |  |  |  | 30 |  | 1170 | 3.0682
| 25-69-1065-5-3 |  |  |  |  | 60
| 25-69-1065-5-4 |  |  |  |  | 90 |  |  | log (count) | Average | SD
| 25-69-1065-5-5 |  |  |  |  | 120 |  | 29700 | 4.4728 | 4.4517 | 0.03035 | 1.0044 | 0.051721
| 25-69-1065-5-6 |  |  |  |  | 150 |  | 27600 | 4.4409
2015-06-23 | 26-amb-1065-5-1 | 26 | Ambient | 1065 | 5 | 0 |  | 26500 | 4.4232
| 26-amb-1065-5-2 |  |  |  |  | 30 |  | 26100 | 4.4166
| 26-amb-1065-5-3 |  |  |  |  | 60 | Triplicate assay | 28900 | 4.4609
| 26-amb-1065-5-4 |  |  |  |  | 90 |  | 31300 | 4.4955
| 26-amb-1065-5-5 |  |  |  |  | 120
| 26-amb-1065-5-6 |  |  |  |  | 150 |  |  | log (count) | Average | SD
[8 empty] | 298000 | 5.4742 | 5.456 | 0.021372
[8 empty] | 260000 | 5.415
[8 empty] | 292333.3333 | 5.4659
[8 empty] | 288000 | 5.4594
[8 empty] | 284000 | 5.4533
[8 empty] | 294000 | 5.4683
Average SD
0.15402
Note on H5: Peter Sanciolo: Start of timing after 3 x HRT has passed after start of injection of MS2.

## Calc. Ventura Val.
Pooled Data | [13 empty] | Temperature
2015-04-24 |  |  |  | 2015-05-27 |  |  | 2015-06-02 |  |  | 2015-06-23 |  |  | Test Date | 75 | 72 | 69
Temp ( C ) | MS2 count (pfu/mL) | log (count) | LRV | MS2 count (pfu/mL) | log (count) | LRV | MS2 count (pfu/mL) | log (count) | LRV | MS2 count (pfu/mL) | log (count) | LRV | 2015-04-24 | 4.5438 | 2.1232 | 0.71338
75 | 0.3 | -0.52288 | 4.5438 | 1.7 | 0.23045 | 5.2035 | 5 | 0.69897 | 4.7349 | 1.2 | 0.079181 | 5.3547 |  | 4.0209 | 2.1178 | 0.81405
| 1 | 0 | 4.0209 | 1.3 | 0.11394 | 5.32 | 1.8 | 0.25527 | 5.1786 | 3 | 0.47712 | 4.9568 |  | 4.0209 | 2.208 | 0.73531
| 1 | 0 | 4.0209 | 2 | 0.30103 | 5.1329 | 7 | 0.8451 | 4.5888 | 1 | 0 | 5.4339 |  | 4.7198 | 2.3219 | 0.73757
| 0.2 | -0.69897 | 4.7198 | 1 | 0 | 5.4339 | 2 | 0.30103 | 5.1329 | 0.7 | -0.1549 | 5.5888 |  | 3.7198 | 2.1232 | 0.72421
| 2 | 0.30103 | 3.7198 | 1 | 0 | 5.4339 | 1.5 | 0.17609 | 5.2578 | 0.3 | -0.52288 | 5.9568 |  | 4.3731 | 2.3488 | 0.73084
| 0.44444 | -0.35218 | 4.3731 | 2 | 0.30103 | 5.1329 | 2 | 0.30103 | 5.1329 | 1 | 0 | 5.4339 | 2015-05-27 | 5.2035 | 2.2972 | 0.85413
[14 empty] | 5.32 | 2.5201 | 0.72634
[14 empty] | 5.1329 | 2.3405 | 0.70964
72 | 79 | 1.8976 | 2.1232 | 1370 | 3.1367 | 2.2972 | 1110 | 3.0453 | 2.3886 | 920 | 2.9638 | 2.4701 |  | 5.4339 | 2.4516 | 0.85413
| 80 | 1.9031 | 2.1178 | 820 | 2.9138 | 2.5201 | 1210 | 3.0828 | 2.3511 | 1150 | 3.0607 | 2.3732 |  | 5.4339 | 2.7527 | 0.80045
| 65 | 1.8129 | 2.208 | 1240 | 3.0934 | 2.3405 | 1190 | 3.0755 | 2.3584 | 950 | 2.9777 | 2.4562 |  | 5.1329 | 2.4562 | 1.1117
| 50 | 1.699 | 2.3219 | 960 | 2.9823 | 2.4516 | 1380 | 3.1399 | 2.294 | 1030 | 3.0128 | 2.4211 | 2015-06-02 | 4.7349 | 2.3886 | 1.0628
| 79 | 1.8976 | 2.1232 | 480 | 2.6812 | 2.7527 | 1300 | 3.1139 | 2.32 | 1020 | 3.0086 | 2.4253 |  | 5.1786 | 2.3511 | 1.0074
| 47 | 1.6721 | 2.3488 | 950 | 2.9777 | 2.4562 | 1530 | 3.1847 | 2.2492 | 1170 | 3.0682 | 2.3657 |  | 4.5888 | 2.3584 | 1.0628
[14 empty] | 5.1329 | 2.294 | 0.99934
[14 empty] | 5.2578 | 2.32 | 1.0447
69 | 2030 | 3.3075 | 0.71338 | 38000 | 4.5798 | 0.85413 | 23500 | 4.3711 | 1.0628 | 29700 | 4.4728 | 0.96116 |  | 5.1329 | 2.2492 | 1.0058
| 1610 | 3.2068 | 0.81405 | 51000 | 4.7076 | 0.72634 | 26700 | 4.4265 | 1.0074 | 27600 | 4.4409 | 0.993 | 2015-06-23 | 5.3547 | 2.4701 | 0.96116
| 1930 | 3.2856 | 0.73531 | 53000 | 4.7243 | 0.70964 | 23500 | 4.3711 | 1.0628 | 26500 | 4.4232 | 1.0107 |  | 4.9568 | 2.3732 | 0.993
| 1920 | 3.2833 | 0.73757 | 38000 | 4.5798 | 0.85413 | 27200 | 4.4346 | 0.99934 | 26100 | 4.4166 | 1.0173 |  | 5.4339 | 2.4562 | 1.0107
| 1980 | 3.2967 | 0.72421 | 43000 | 4.6335 | 0.80045 | 24500 | 4.3892 | 1.0447 | 28900 | 4.4609 | 0.97302 |  | 5.5888 | 2.4211 | 1.0173
| 1950 | 3.29 | 0.73084 | 21000 | 4.3222 | 1.1117 | 26800 | 4.4281 | 1.0058 | 31300 | 4.4955 | 0.93837 |  | 5.9568 | 2.4253 | 0.97302
[14 empty] | 5.4339 | 2.3657 | 0.93837
66 | 2800 | 3.4472 | 0.57371 | [9 empty] | Average LRV | 4.9919 | 2.3556 | 0.89951
| 2100 | 3.3222 | 0.69865 | [9 empty] | SD | 0.54889 | 0.13918 | 0.1371 | Average SD | 0.27506
| 1500 | 3.1761 | 0.84478 | [9 empty] | Bottom 5th percentile LRV | 4.0209 | 2.1232 | 0.715
| 1600 | 3.2041 | 0.81675
| 1000 | 3 | 1.0209
| 1400 | 3.1461 | 0.87474
| MS2 count (pfu/mL) | log (count) | Average(log(count)) |  | log (count) | Average(log(count)) |  | log (count) | Average(log(count)) |  | log (count) | Average(log(count))
Ambient | 7300 | 3.8633 | 4.0209 | 253000 | 5.4031 | 5.4339 | 246000 | 5.3909 | 5.4225 | 298000 | 5.4742 | 5.456
| 10900 | 4.0374 |  | 266000 | 5.4249 |  | 272000 | 5.4346 |  | 260000 | 5.415
| 11133 | 4.0466 |  | 264000 | 5.4216 |  | 274000 | 5.4378 |  | 292333.3333 | 5.4659
| 9400 | 3.9731 |  | 270000 | 5.4314 |  | 248000 | 5.3945 |  | 288000 | 5.4594
| 10900 | 4.0374 |  | 269000 | 5.4298 |  | 272000 | 5.4346 |  | 284000 | 5.4533
| 14700 | 4.1673 |  | 311000 | 5.4928 |  | 277000 | 5.4425 |  | 294000 | 5.4683

## Calc. Low before+high after
Pooled Data
| 2015-04-24 |  | 2015-05-27 |  | 2015-06-02 |  | 2015-06-23
Temp (C) | MS2 count (pfu/mL) | log (count) | MS2 count (pfu/mL) | log (count) | MS2 count (pfu/mL) | log (count) | MS2 count (pfu/mL) | log (count) |  | 75C | 72C | 69C | Ambient
75 | 0.3 | -0.52288 | 1.7 | 0.23045 | 5 | 0.69897 | 1.2 | 0.079181 | 2015-04-24 | -0.52288 | 1.8976 | 3.3075 | 3.8633
| 1 | 0 | 1.3 | 0.11394 | 1.8 | 0.25527 | 3 | 0.47712 |  | 0 | 1.9031 | 3.2068 | 4.0374
| 1 | 0 | 2 | 0.30103 | 7 | 0.8451 | 1 | 0 |  | 0 | 1.8129 | 3.2856 | 4.0466
| 0.2 | -0.69897 | 1 | 0 | 2 | 0.30103 | 0.7 | -0.1549 |  | -0.69897 | 1.699 | 3.2833 | 3.9731
| 2 | 0.30103 | 1 | 0 | 1.5 | 0.17609 | 0.3 | -0.52288 |  | 0.30103 | 1.8976 | 3.2967 | 4.0374
| 0.44444 | -0.35218 | 2 | 0.30103 | 2 | 0.30103 | 1 | 0 |  | -0.35218 | 1.6721 | 3.29 | 4.1673
[9 empty] | 2015-05-27 | 0.23045 | 3.1367 | 4.5798 | 5.4031
[10 empty] | 0.11394 | 2.9138 | 4.7076 | 5.4249
72 | 79 | 1.8976 | 1370 | 3.1367 | 1110 | 3.0453 | 920 | 2.9638 |  | 0.30103 | 3.0934 | 4.7243 | 5.4216
| 80 | 1.9031 | 820 | 2.9138 | 1210 | 3.0828 | 1150 | 3.0607 |  | 0 | 2.9823 | 4.5798 | 5.4314
| 65 | 1.8129 | 1240 | 3.0934 | 1190 | 3.0755 | 950 | 2.9777 |  | 0 | 2.6812 | 4.6335 | 5.4298
| 50 | 1.699 | 960 | 2.9823 | 1380 | 3.1399 | 1030 | 3.0128 |  | 0.30103 | 2.9777 | 4.3222 | 5.4928
| 79 | 1.8976 | 480 | 2.6812 | 1300 | 3.1139 | 1020 | 3.0086 | 2015-06-02 | 0.69897 | 3.0453 | 4.3711 | 5.3909
| 47 | 1.6721 | 950 | 2.9777 | 1530 | 3.1847 | 1170 | 3.0682 |  | 0.25527 | 3.0828 | 4.4265 | 5.4346
[10 empty] | 0.8451 | 3.0755 | 4.3711 | 5.4378
[10 empty] | 0.30103 | 3.1399 | 4.4346 | 5.3945
69 | 2030 | 3.3075 | 38000 | 4.5798 | 23500 | 4.3711 | 29700 | 4.4728 |  | 0.17609 | 3.1139 | 4.3892 | 5.4346
| 1610 | 3.2068 | 51000 | 4.7076 | 26700 | 4.4265 | 27600 | 4.4409 |  | 0.30103 | 3.1847 | 4.4281 | 5.4425
| 1930 | 3.2856 | 53000 | 4.7243 | 23500 | 4.3711 | 26500 | 4.4232 | 2015-06-23 | 0.079181 | 2.9638 | 4.4728 | 5.4742
| 1920 | 3.2833 | 38000 | 4.5798 | 27200 | 4.4346 | 26100 | 4.4166 |  | 0.47712 | 3.0607 | 4.4409 | 5.415
| 1980 | 3.2967 | 43000 | 4.6335 | 24500 | 4.3892 | 28900 | 4.4609 |  | 0 | 2.9777 | 4.4232 | 5.4659
| 1950 | 3.29 | 21000 | 4.3222 | 26800 | 4.4281 | 31300 | 4.4955 |  | -0.1549 | 3.0128 | 4.4166 | 5.4594
[10 empty] | -0.52288 | 3.0086 | 4.4609 | 5.4533
| MS2 count (pfu/mL) | log (count) | [7 empty] | 0 | 3.0682 | 4.4955 | 5.4683
66 | 2800 | 3.4472
| 2100 | 3.3222 | [6 empty] | Average LV | 0.088728 | 2.7251 | 4.1811 | 5.0833
| 1500 | 3.1761 | [6 empty] | SD | 0.36394 | 0.54826 | 0.54198 | 0.62877
| 1600 | 3.2041 | [6 empty] | Average LRV | 4.9946 | 2.3583 | 0.90217
| 1000 | 3
| 1400 | 3.1461 | [6 empty] | Top 5th percentile LV | 0.66569 | 3.1394 | 4.6965
[9 empty] | Bottom 5th percentile LV |  |  |  | 3.9828
| MS2 count (pfu/mL) | log (count) |  | log (count) |  | log (count) |  | log (count) | Bottom 5th percentile LRV | 3.3171 | 0.84337 | -0.71368
Ambient | 7300 | 3.8633 | 253000 | 5.4031 | 246000 | 5.3909 | 298000 | 5.4742
| 10900 | 4.0374 | 266000 | 5.4249 | 272000 | 5.4346 | 260000 | 5.415
| 11133 | 4.0466 | 264000 | 5.4216 | 274000 | 5.4378 | 292333.3333 | 5.4659
| 9400 | 3.9731 | 270000 | 5.4314 | 248000 | 5.3945 | 288000 | 5.4594
| 10900 | 4.0374 | 269000 | 5.4298 | 272000 | 5.4346 | 284000 | 5.4533
| 14700 | 4.1673 | 311000 | 5.4928 | 277000 | 5.4425 | 294000 | 5.4683